## Introduction
Vegetable Growers - Energy Saving Opportunities
These opportunities have been identified in a series of energy audits of vegetable growers and are not meant to be comprehensive or accurate for individual growers.
Use these as a guide and then determine the costs and benefits for your own circumstance if it is considered worth pursuing.
STEPS:
1. Determine your own costs of energy (electricity, diesel and LPG)
2. Enter these costs at the head of the sheet concerned in the yellow cells
3. Review the costs (CAPEX = capital expenditure and OPEX = operational costs per year) which can be changed to suit your own circumstances
4. Review the calculations and if not sure contact the originator for details of the calculation method
5. Determine the suitability of the opportunities
6. If an opportunity is considered worth pursuing we strongly recommend a new analysis of costs and benefits is undertaken before deciding whether to implement the opportunity
The sheets have been split into key operations for ease of use of the sheet concerned.
Use the tabs at the bottom to source a particular operation, or use the "full calculations" list
Further information is available from:
Infotech Research - contact John Cumming on 03) 98677446 / 0418 125688
or email - john@infotechresearch.org

## Full Calculations
|  | PLEASE ENTER THE COST TO YOUR BUSINESS (or operational area) OF EACH ENERGY SOURCE |  |  | $/L or kWh | 0.25 | 1.4 | 0.95 |  |  |  | CAPEX / OPEX can be modified as determined in individual cases | Savings are estimated from the actual GJ energy savings + Other savings - OPEX if applicable Payback is calculated from the capital cost / savings per year | Conversion factors: LPG density 0.518 kg/L 0.0257 GJ/L Diesel 0.850 kg/L 0.0386 GJ/L Electricity 0.0036 GJ/kWh
Opportunity Name | Plant Area | Description | Project Type | Project Cost ($) CAPEX | Project cost ($) OPEX | Electricity Savings (GJ/y) | Diesel Savings (GJ/y) | LPG Savings (GJ/y) | Other Savings ($) | Savings ($) | payback years | Comments | Calculation Description | Assumptions | Refs
Electric forklifts | Alternative energy sources | Electric forklifts can be charged on weekends and evenings for day operations with the aid of battery system and PV back-up | Energy storage | 20000 | 250 | -36.9 |  | 109.225 | 1500 | 2723.7049 | 7.3429 | Costs and savings are per electric forklift operating 250 x8 hour shifts per year | 41 kWh/shift (service $250/y) LPG 17 L/shift (service $1500/y) | 25c/kWh = $69.44/GJ and LPG $1/L = $38.9/GJ | Yale Materials Handling Corp.
Solar panels on roof | Alternative energy sources | Reduce peak electricity demand with solar generation | Demand reduction | 40000 | 0 | 129.6 |  |  |  | 9000.72 | 4.4441 | 20 kW system installed | $2/W installed, 6h/day over 300 d/y x 20 y | 25c/kWh = $69.44/GJ all solar energy replaces that bought from the grid
Wind power source | Alternative energy sources | Reduce peak electricity demand with wind generation | Demand reduction | 390000 | 20000 | 1420 |  |  |  | 78619 | 4.9606 | Wind requirements are critical to economics of wind generation - need 20% of capacity at 4.5 to 5 m/s | Capital cost of a 225 kW system = $390,000 Subsidies LGCs continue at 2014 rate | Assume 20% of capacity achieved Cost per kW for a second hand system of $1,750/kW OPEX at 5% p.a.
Batteries for energy storage | Alternative energy sources | Spread the electricity demand using Lithium Ion batteries 100 kWh system installed | Demand reduction | 100000 | 1000 | 108 |  |  |  | 6500.6 | 15.3832 | Additional savings may be made by reducing peak demand charges. CAPEX reduction is likely as battery production increases | Total energy saved and reused = 100*0.9*5000 = 450,000 kWh = 30,000 kWh/y = 108 GJ/y Cost = $10 x 100 kWh = $1000/y | 1 cycle per day to 90% of capacity over 5,000 cycles Battery efficiency 90% O&M cost of $10/kWh/y Cost of LIB at $1000/kWh and cost of power dsicounted from a solar or wind system. | http://theenergycollective.com/schalk-cloete/421716/seeking-consensus-internalized-costs-energy-storage-batteries
Blowdown heat recovery | Boiler | Install a flash vessel to recover waste heat from boiler blow down | Energy Efficiency | 8500 |  |  |  | 85.32 |  | 3153.0006 | 2.6958 | Energy savings and paybacks are dependent on the size of the boiler system employed |  | LPG usage on site is assumed 80% of this is use by a boiler and the rest been used by forklifts. The saving are estimated at 3% for the installation of a Flash vessel, this is the industry norm | saving based on Best Practice Guide Steam, Hot Water & Process Heating -- Sustainability Vic
Boiler Management system | Boiler | Install a Boiler Management system that controls the air to fuel mixture to ensure complete consumption of fuel | Energy Efficiency | 10500 |  |  |  | 142.2 |  | 5255.001 | 1.9981 | Energy savings and paybacks are dependent on the size of the boiler system employed |  | The saving are estimated at 5% for the installation of a boiler management system | saving based on Best Practice Guide Steam, Hot Water & Process Heating -- Sustainability Vic
Economisers | Boiler | Install an Economiser is to the boiler flue, to recover waste heat. The waste heat could be used to pre heat boiler make up water | Energy efficiency | 12200 |  |  |  | 142.2 |  | 5255.001 | 2.3216 | Energy savings and paybacks are dependent on the size of the boiler system employed |  | The savings are estimated at 5% for the installation of an economiser, this is an industry norm | saving based on Best Practice Guide Steam, Hot Water & Process Heating -- Sustainability Vic
Pre heat combustion air | Boiler | Use waste heat to pre heat combustion air before feeding in to the boiler | Energy efficiency | 4500 |  |  |  | 56.88 |  | 2102.0004 | 2.1408 | Energy savings and paybacks are dependent on the size of the boiler system employed |  | The saving are estimated at 2% for installation of combustion air pre heating
Total dissolved solids (TDS) control, and boiler blowdown | Boiler | Install automated TDS control system, to reduce the amout of blow down required. Saving both energy, and boiler treatment chemicals | Energy and water efficiency | 3560 |  |  |  | 56.88 |  | 2102.0004 | 1.6936 | Energy savings and paybacks are dependent on the size of the boiler system employed |  | VSD drive $525 / 5.5 kW = $95/kW Installation and control = $100/kW The saving are estimated at 2% from the installation of a TDS control system. This doesn't take into account the saving in boiler chemicals
Chiller fan demand reduction | Chillers | Set up a fan cycling system or VSDs on all fans so that they even out the demand and maintain heat exchange | Cooling efficiency | 526.5 | 0 | 7.3872 |  | 0 |  | 513.041 | 1.0262 | VSD operating on a bank of 6 x 0.45 kW condenser fans | Evening out of operation save 4% energy VSD saves 15% of energy by fan motors | VSD drives saves 15% energy in the duty cycle Additional savings of 4% are from temperature stabilisation
Chiller VSDs | Chillers | VSDs can be added to the compressors and condenser fans to enable a variable refrigeration supply to the cool rooms | Cooling efficiency | 1940 |  | 13.68 |  | 0 |  | 950.076 | 2.0419 | VSDs can be added to compressor and fan motors as long as they are suitably insulated. If not a filter has to be added | A 10 kW compressor running at 80% of capacity will consume about 20,000 kWh/y at 8kW demand Savings in motor efficiency at a set temperature average 15% with a further 4% savings in on/off losses | All of the waste heat is able to be utilised in the absorption chiller. COP of the conventional compression chillers averages 2.0. | Kirby-Titan information
Investigate possibility of using Absorption Chillers | Chillers | If the site generates waste heat this can be combined with solar heating systems to drive a absorption chiller system | Energy efficiency | 150000 |  | 180 |  | 0 |  | 12501 | 11.999 | Absorption chiller units are all imported and may be considerably cheaper if direct importation is undertaken | The waste heat is estimated at 20% of the heating energy of 2,800 GJ/y. Giving approximately 600 GJ of waste heat in one year. The COP of absorption chillers is about 0.6 and the cost is estimated at $6,000 per kWr. This is assumed to replace 25 kW of conventional chillers
Move from R22 refrigerants | Chillers | Replace R22 with less polluting alternatives | Greenhouse emissions | [6 empty] | 0 | N/A | Phase out of R22 is in progress as it is a strong Greenhouse gas and ozone depleting substance |  | Solar energy collected = 10kW x 2,000 h/year COP of the absorption system is 0.6 Cost of power saved is 25c/kWh
Solar energy absorption chiller system | Chillers | Installation of a solar absorption chiller could be considered to reduce cooling energy use | Energy sources | 60000 | 0 | 43.2 |  | 0 |  | 3000.24 | 19.9984 |  | 10 kW system using evacuated tube panels at $6,000 per kWr | Assume operation of chiller 250 days Chiller cooling at COP = 2.0
Sun shield for chiller units | Chillers | Install a roof over chillers to reduce the heat load on them by reflecting the sun's energy away from the chiller. | Cooling efficiency | 250 |  | 1.0674 |  | 0 |  | 74.1309 | 3.3724 |  | Radiant energy 1120W/m2 at 53% IR Ave 0.593kW/m2 x 2m2 x 6h/d x 250 d/y | Old chiller's COP = 0.7 New scroll compressor COP = 3.0 Actual drive kW at 80%of max.
Chiller unit rationalisation | Chillers | Replace a group of small chillers with one larger unit that is more efficient | Energy efficiency | 21600 |  | 90.7 |  | 0 |  | 6299.115 | 3.4291 | The combination of 3 old 7.5 kWunits into one new 10 kW chiller CAPEX based on Coolpak system 40 plus $4,500 installation | COP for old units at 0.7 and the new unit 3.0 Running both systems at 50% of time over 30 weeks per year | 9 chillers operating at an efficiency COP of 1.5 ave To one chiller with controller at COP of 4.0 | Solar Cooling in Aust. By Kohlenbach and Dennis - Ecolibrium PP32, December 2010
Replacement of old chiller compressors | Chillers | Any chiller system over 15 years old can be economically replaced with a new more efficient unit | Energy efficiency | 4500 |  | 21.6 |  | 0 |  | 1500.12 | 2.9998 | Replacement of a 7 kW compressor at COP of 0.7 with a new 2 kW unit at COP of 3. | A 7 kW compressor at 80% of capacity for 30 h/week x 50 w/y = 8,400 kWh A replacement system at 2 kW for the same operating period = 2,400 kWh Saving = 6,000 kWh =21.6 GJ
Glycol cooling storage | Chillers | Use time of low electrical tariff and periods when solar electricity cannot be used, to store cooling in the form of a glycol or salt block | Energy efficiency and cost efficiency | 9500 |  | 0 |  | 0 |  | 0 | N/D |  |  | Assume: COP of chillers is 1.5 Cost of plumbing and control gear and tank is $800/kW 50 kW of solar power is available for 8 hours per day on weekends
Glycol cool storage 2 | Chillers | Use solar power otherwise wasted to run chillers and generate cool storage in the form of glycol/water ice. Run this back through a heat exchanger to lower the load on chillers | Energy storage | 40000 |  | 145 |  | 0 |  | 10070.25 | 3.9721 | Solar power may be wasted during the weekend or at times of low production. Ice storage in glycol systems may act as energy storage | Chillers run at a total of 50 kW to cool glycol tank over 16 hours during the weekend giving 800 kWh of cooling energy at COP of 1.5 = 1200 kWh or 4.3 GJ of sensible cooling from solar power (min 50 kW PV rating). Savings of 2.9 GJ/week | All compressed air system have leaks, best practices is 3% loses due to leak. The majority of systems have between 20% and 50% loss due to leaks. For the purpose of these calculation we have assumes 30% loss due to leaks.
Leaks | Compressed air | Reducing air leaks to reduce the load on the compressor and save compressed air energy | Energy efficiency | 420 |  | 15.3 |  |  |  | 1062.585 | 0.39526 | Air leaks are always economic to fix | Assuming compressor is a 7.5KW running at a 70% load running 56hr a week, 48 week a year. – 14112 kWh/ year (51GJ) - at $0.20 per kWh = $2822.4 | Chiller COP = 2.0 Cool store is run 365 days per year Ambient to cool store temperature difference is 23 C Cost of power is 25c/kWh
Cool room floor insulation | Cool stores | Cooling loss can be reduced with floor insulation using a 10mm rubber roll stuck to the concrete base | Energy efficiency | 3900 | 0 | 280.8 |  | 0 |  | 19501.56 | 0.19998 | Using a cool store with a floor area of 156 m2. | Slab conductance is 230 W/m2 at delta T -= 23 C Addition of 10mm rubber decreases this to 109 W/m2 | COP of refrigeration system is 2.0 COP = 2.0 Chilled water used = 6,000 L/h Filtration and treatment for recycling costs $35,000 + $12,000 per year in chemical and maintenance
Cold water recycling | Cold flumes | Cold water used for hydro coolers and fluming can be filtered and recycled to reduce refrigeration loads | Recycling | 35000 | 12000 | 912 |  | 0 |  | 51338.4 | 0.68175 | This can save significant amounts of refrigeration energy if cold water recycling is not practised | Cooling energy used in cooling unrecycled water is 6,000 L/h x 4.12 kJ/kg.K x T (25-2) = 570 MJ/h. Refrigeration energy is 285 MJ/h. Recycling this water through a filter system saves 80% of this energy = 228 MJ/h = 912 GJ/year | Costs estimated at $15/L and a coverage of 16m2/L with two coats = $188 + painter at $200. | Rotating drum filter systems are available through Wyma
Paint roof white over the cool room and the chillers | Cool stores | White paint will reflect the sun light and lower the temperature gradient between outside and inside | Insulation | 388 |  | 9.6 |  | 0 |  | 666.72 | 0.58195 | Calculation on 100 m2 of roofing | Approximate heat rejection of 178W/m2 for 6h/d x 250 d/y = 267 kWh/y/m2. Over a roof area of 100m2 gives a heat rejection of 26.7 MWh/y . 20% of this removed by cooling system at a COP of 2.0 takes 2,670kWh/y | 2.5 kW fan cost $850 Installation $850 COP of refrigeration chiller = 2.0 | NXTCool Zone from Nutech Paint
Reduce the number of evaporator fans | Cool rooms | Fan heat can be reduced by using less fans with a larger capacity | Energy efficiency | 1700 |  | 2.952 |  | 0 |  | 205.0164 | 8.292 | Calculation for one bank of 6 x 0.45 kW fans at an efficiency of 80% replaced with 1 x 2.5 kW fan at 90% efficiency | Fan energy consumption saving per bank = 10% of 2.7 kW = 0.27 kW Refrigeration load reduction of 0.27 kW of heat per bank /COP of 2.0 = 0.14 kW Cool room operation of 40 hours/week x 50 weeks per year = 820 kWh/y | Chiller operation 50% of the day 7 days x 30 weeks per year at 150 W avoided. Cost of barrel fan and ducting estimated for one room at $1500
Replace room fans with external barrel fans and ducts | Cool stores | Barrel fans external to the cool store reduces heat input to the cool store and enables ducting of air for optimal circulation | Energy efficiency | 1500 |  | 1.3608 |  | 0 |  | 94.5076 | 15.8717 | Cool store evaporative fans produce 15% of energy input into heat in the room | Bank of 4 x 0.25 kW evap. fans add 150W of heat into the room. This requires 214 W of extra cooling energy at a COP of 0.7 costing 5.3c/h. This can be totally avoided by placing the fans outside the cool room | Fans run 70% of 24 h/7d/30 w/y VSD cost = $250/kW + $200/kW installation
Variable speed drive applied to the cool room evaporator fans | Cool stores | The air circulation can be reduced using a VSD on the fans which will reduce cold air loss in the cool room and save energy at the chillers | Energy efficiency | 900 |  | 8.3825 |  | 0 |  | 582.1666 | 1.5459 | Calculation for 2kW of evaporator fans. Power consumption by fans varies as the fan speed cubed | VSD control on evaporator fans saves 4% on stability of temperature control, 25% on fan VSD energy consumption due to VSD control and a further 3.75% due to fan heat reduction. Savings total 33% for a bank of 8 x 0.25 kW fans = 0.66kW |  | http://www.airah.org.au/imis15_prod/Content_Files/EcoLibrium/2013/Apr13/EcoApril13_Forum.pdf
Rapid closing doors on the cool store | Cool stores | Cold air lost when the cool room doors are open during forklift movements in and out can be reduced with rapid closing roller doors | Reduce energy loss | 18000 | 150 | 18.98 |  |  |  | 1168.161 | 15.4088 | Based on a cool room of 700 m3 running continuously at an average ambient temperature of 25 C and a set temperature of 2 C | Savings estimated at 50% of convective losses that total 8% of the total cooling load, calculated at 1.3 GJ/day | Doorway losses are reduced by 30% during opening doorway losses total 8% or 1.3 GJ of cooling load/day
Link evaporator fan operation to door opening | Cool stores | Evaporator fans do not run when the doorway is open as they assist in circulating the air out through the doorway | Reduce energy loss | 400 |  | 7.8 |  | 0 |  | 541.71 | 0.7384 | Reed switch is placed on the door which is connected to the power source for the evaporator fans | Doorway losses of energy are reduced by 30% of 8% of 1.3 GJ/day = 0.0431 GJ/day Cool store operation is during work days (250 per year) Savings = 0.031 x 250 GJ/y = 7.8 GJ/y | Door way energy losses are 1.3 GJ/day
Apply VSD to AHU fans | Cool stores | Use VSDs to reduce AHU fans velocities after cooling and at night | Cooling efficiency | 1177.5 | 0 | 9.5256 |  |  |  | 661.5529 | 1.7799 | Calculation = per AHU fan The need to run AHU fans at peak power diminishes as the produce reaches the desired temperature | VSD installed cost = $195/kW plus temperature control system at $300 which saves an estimated 25% of fan power demand. Assumed fan usage is 50% of time over 35 weeks/y | Heat capacity in total is 150 MJ/K Temperature cycle is 3 K (0.5 over night to 3.5 at end of day) Cost of implementation is PLC on temp control programmable for $5,000
Cycle cool room temperature settings | Cool stores | Increase cooling during the night time and allow cool rooms to rise in temperature during the day to save energy and move consumption to off-peak | Cool room efficiency | 5000 |  | 375 |  |  | 3127.5 | 29171.25 | 0.1714 | Temperature cycling will work when the off-peak tariff operates and there is considerable heat capacity in the cool room contents (ie uninsulated concrete flooring) | Energy savings in cooling = delta T ambient of 15 K x 150 MJ plus Cost savings of extra cooling of 3K x 150 MJ at $27.8/GJ | 70% saving of cold air losses of 35 MJ/day Capital cost $2,500 + $1,500 installation Running cost ( doorway linked) at $200 p.a.
Use of air curtains at cool store openings | Cool stores | Air curtain directed vertically down at entrance to minimise air movement out of the cool store | Cool room efficiency | 4000 | 200 | 6.125 |  | 0 |  | 225.3812 | 17.7477 | Air curtains are more effective in holding cool air than plastic strips and prevent icing up around doorways | 70% of 35 MJ/day x 250 d/.y at $69.44 per GJ | 35 MJ/day losses through the doorway 250 days per year operation 50% savings be using plastic strips
Plastic curtains | Cool stores | Use of plastic strips to prevent air movement when cool room doors are open | Cool room efficiency | 500 | 50 | 4.4 |  | 0 |  | 255.58 | 1.9563 | This calculation is based on 3 air changes per day in the cool room | 3% of energy used to replace losses through the cool room doorways = 35 MJ/day for 250 days per year for a 700 m3 cool room at 2C = 4.4 GJ/y savings | Cost of Peak electricity $0.30 per KW/Hr Off Peak is $0.10 per Kwan hour at present the chiller run use 60% peak and 40% off Peak The new system would run 30% peak and 70% off peak The system use a 10Kw chiller cooling a 15m x 8m @ 1 C Cool room - and use 41, 833 KW/Hr per year | Australian Refrigeration and Air Conditioning Vol 2.
Off-peak and week-end energy storage | Cool stores | An additional thermal store, in the form of frozen glycol or salt, can be established to store solar power when not used by operations. This can be bled back into the cooling system during operations | Energy efficiency and cost efficiency | 9500 |  | 0 |  |  |  | 0 | N/D |  |  | That there is a 0.005% loss of energy when the cool room door is opened when the sensors are tripped by passing traffic. The sensors are tripped 30 times per day over 250 days per year
Set up forklift movement controls | Cool stores | Prevent forklifts inadvertently tripping sensors and opening cool room doors by protecting the sensor area or placing signage on the ground | Loss prevention | 500 |  | 4.7988 |  |  |  | 333.2767 | 1.5003 | Forklift passing traffic can be directed around the door sensors with barriers either side of the door. A less effective alternative is signage painted on the ground where the sensors are | Chillers use 26601KW/hr a year, by stopping unintended door openings a saving of 0.005% can be achieved each time. Cost of electricity is $0.30per kWh | Conduction loss in cool store superstructure 10 kWh/d The cost of construction of internal PU foam walls and ceiling saves 80% of this. Construction cost is $5,000
Old cool store upgrades to improve insulation | Cool stores | Converted cool stores can show high temperature variation on the external cladding. Construction of inner foam walls and ceiling will save energy | Energy efficiency | 5000 |  | 7.2 |  | 0 |  | 500.04 | 9.9992 | Each converted cool store requires individual evaluation of costs and benefits | 10 kWh/day at 250 days operating per year = energy loss 80% of this is saved = 2,000 kWh/y at25c/kWh = $500/y | Losses due to a lack of sealing = 30% of an open doorway = 42 MJ/day 250 operating days per year COP of refrigeration system = 0.7
Truck seal during loading | Dispatch - cool stores | Air leakage during truck loading can be minimised with a flexible sealing system | Energy efficiency | 3500 |  | 4.5 |  | 0 |  | 312.525 | 11.1991 | Sealing losses will be dependent of product movement and the number of trucks loaded as such the cost benefit is uncertain | Sealing saving = Energy losses/day x days /COP of refrigeration system
Demand management system | Electricity supply | Demand management systems are used to shift energy loads from periods of high cost to periods of lower cost. This can be achieved by production planning, peak load shedding and additional sources of energy from solar, wind or batteries | Peak load reduction | [6 empty] | 0 | N/D | This can be a very efficient way of saving energy costs |  | Assume Power factor is corrected from 0.7 to 0.95 on a 100 kVA supply running on average at 50 kVA Peak kVA charge is $10/kW/day Cost of PF correction is $25,000
Power Factor correction | Electricity supply | Peak demand can be reduced by applying capacitors to compensate for reactive load | Peak load reduction | 25000 |  | 0 |  | 0 | 45625 | 45625 | 0.54795 | Power factor correction economics depend on demand costs and the state of the power factor before correction | Cost savings = 100*0.25*10*365/2
Heat exchange cold water with incoming fresh water | Flumes | Use chilled water wastes to cool incoming town water and reduce the load on chillers cooling incoming water | Energy usage efficiency | 7500 |  | 25.6 |  | 0 |  | 1777.92 | 4.2184 |  |  | Plastic blind cost = $500 fitted COP refrigeration = 2.0 80% saving of cold water loss through blinds
Hydro cooler plastic blinds | Hydro cooler | Replace plastic strips with pull down plastic blinds to contain the cold water and reduce loss | Energy loss reduction | 500 |  | 40 |  | 0 |  | 2778 | 0.17999 | Losses measured of 10L/min with a temperature of 2C were estimated during hydro cooler operation | Cold water refrigeration losses = 10L/min x 20K x 4.12 kJ/kg.K x 60 min/h = 50 MJ/h Saving 80% of loss = 40 MJ/h / COP of refrigeration of 2.0 = 20 MJ/h = 40 GJ/y of electricity to the chiller | Insulation is 80% efficient at reducing thermal losses. Conductance for SS 18 W/mK Cooling water temp = 2C, steel at 6C and ambient temp = 30C Temperatures maintained for 6,000 h per year. Refrigeration COP = 2.0
Hydro cooler thermal insulation | Hydro cooler | Reduce conductive and radiant losses from steel vessels and pipe work with spray on insulation (PU) and spacer isolation from the floor | Insulation | 12000 |  | 130.464 |  | 0 |  | 9060.7248 | 1.3244 | Various types of insulation can be applied from lagging, to stick-on and spray on insulation. The costs vary and access and cleanliness are key considerations | Conduction Q= k delta T. A/s (where Q is the heat flow, T degrees K, A is the surface area and s is the thickness) = 18x24x0.05/0.02 = 1.1 kW per flanged leg x 8 legs = 8.8 kW Radiation loss at 2C and delta T 24C ~ 150 W/m2 x 30m2 = 4.5 kW for hydro cooler Steel pipe work radiative loss = at 150 W/m2 x 0.6 m(200mm pipe) x 20m = 1.8 kW
Insulation of cooling water pipe work | Hydro cooler | Insulation of exposed cooling water pipes | Insulation | 2400 |  | 30 |  | 0 |  | 2083.5 | 1.1519 |  | The chiller use 41,833 KW/hr a year @ an average cost of $0.25 KW/hr =$10,458.25 | Vessel temperature 6C Vessel surface area = 32 m2 Operation all year = 6,000 h COP of refrigeration system is 2.0 | http://www.engineeringtoolbox.com/thermal-conductivity-d_429.html
Thermal insulation of cold water buffer vessels | Hydro cooler | Insulation of exposed surfaces and stands for cooling vessels | Insulation | 5500 |  | 79.488 |  | 0 |  | 5520.4416 | 0.9963 | Spray insulation should be adequate if access to the steel surfaces is not required | Conduction losses of 1.1kW per stand leg = 4.4 kW Radiant loss from exposed surfaces at 150 W/m2 x 32m2 = 4.8kW 80% saved by insulation of stand and vessel walls | Plastic blind cost = $500 fitted COP refrigeration = 2.0 80% saving of cold water loss through blinds | http://en.wikipedia.org/wiki/List_of_thermal_conductivities
Hydro cooler plastic blinds | Hydro cooler | Replace plastic strips with pull down plastic blinds to contain the cold water and reduce loss | Energy loss reduction | 500 |  | 40 |  | 0 |  | 2778 | 0.17999 | Losses measured of 10L/min with a temperature of 2C were estimated during hydro cooler operation | Cold water refrigeration losses = 10L/min x 20K x 4.12 kJ/kg.K x 60 min/h = 50 MJ/h Saving 80% of loss = 40 MJ/h / COP of refrigeration of 2.0 = 20 MJ/h = 40 GJ/y of electricity to the chiller | Heat capacity 4.12 kJ/kg-K Heat exchanger efficiency 80% Cool water dump weekly Installed cost shell and tube exchanger $10,000
Energy recovery from cold waste | Hydro cooler | Heat exchange waste cold water discharged from the hydro cooler with incoming water into a cold water storage tank | Energy and resource efficiency | 27500 |  | 38 |  | 0 |  | 2639.1 | 10.4202 | The payback will be considerably better if the plumbing and cold water tank are already installed. | 30 m3 of stored water at 2C is dumped per day and exchanged with incoming water at 25C, which is dropped to 15C through a heat exchanger saving 0.96 GJ of energy per dump x 40 dumps per year = 38 GJ/y at a COP of 1.0 for the refrigeration system | Cooling water = 100 kL/day Temperature = 6C outgoing, 20C incoming Exchanger efficiency 46% Cost of exchanger $12,000 + insulated tank = $5,500 + plumbing and controls = $10,000 | Product and Process Design http://www.seas.upenn.edu/~dlewin/FOCAPD_2004/LECTURE_06_Equipment_Sizing_and_Capital_Cost_Estimation.pdf
Cold water heat exchange | Hydro cooler | When chilled water is dumped a heat exchanger can be used to cool feed water into a cold water tank for use across the site | energy recovery | 27500 |  | 334.8 |  | 0 |  | 23251.86 | 1.1827 | This opportunity is applicable if cold water recycling is not practised | Potential energy saved = 100,000 L/d x 4.12 x 14K = 5,880 MJ/day Heat exchanger recovery at 46% = 2,704 MJ/day = 751 kWh/day COP refrigeration system = 2.0 actual refrigeration saving = 372 kWh/day = 93,000 kWh/ 250 day year | Pipe lagging cost $250 and saves 80% of the heat transfer Radiant heat/cool losses 150W/m COP of vac cooler = 1.0 | Product and Process Design http://www.seas.upenn.edu/~dlewin/FOCAPD_2004/LECTURE_06_Equipment_Sizing_and_Capital_Cost_Estimation.pdf
Insulation of cooling water pipe work | Hydro vac cooler | Insulation of exposed cooling water pipes | Insulation | 250 |  | 0.648 |  | 0 |  | 45.0036 | 5.5551 |  | 150 W x 5 m x 2h/day x 150 days/y = 225 kWh/y saving 80% = 180 kWh/y | 5 kW bore pump utilising a 5 kW array Providing useful water to a dam 80% of the year Replacement of the same pump using electrical supply | http://www.engineeringtoolbox.com/thermal-conductivity-d_429.html
Solar bore pumps | Irrigation | Solar bore pumps can be added to the existing dam supply with the saving of bore pump energy and cost | Energy source | 12500 |  | 24.192 |  | 0 |  | 1680.1344 | 7.4399 | Specifically designed solar bore pumps are available and can use direct DC motor to solar panel connections. Operation is only during daylight hours | 5 kW array costs $2.50/W including installation (using STC subsidies) The pump operates 8 hours/day 30 weeks of the year using 6,720 kWh/y at 80% of capacity all of which is saved by the solar system | Conversion to a direct coupling costs $2,000 Power cost at 25c/kWh | NSW Farm Innovation Program 2013 - Solar Pumping Systems
Replace belt drive pump couplings with direct drives | Irrigation | Redesign the pump coupling to direct through a gearbox for belt drives | Energy efficiency | 2000 |  | 16.2 |  |  |  | 1125.09 | 1.7776 | Gear box losses are about 10% of fan belts, so a 10% efficiency loss through a fan belt can be reduced to 1% through a gear box | 55kW pump losses 10% of its efficiency at 55 x 40h x 30weeks/y = 5,000 kWh a gear box direct drive will reduce this to 1% - 500 kWh overall saving is 4,500 kWh/y | Submersible at 5 kW in the river operates 40 h/week and 25 weeks per year at 80% of capacity (dynamic head reduction of 10m = 100 kPa) Pressure pump efficiency raised 15% (45 kW) Submersible pump cost is $2,540 + fitting $1000
Irrigation booster pumps | Irrigation | Install submersible pumps in storages with the pressure pumps on the banks to increase the flow rates | Energy efficiency | 3540 |  | 5.4 |  |  |  | 375.03 | 9.4392 | A low pressure high flow submersible pump can reduce the suction head and improve the main pump performance | Submersible energy consumption = 4,000 kWh/y Pressure pump savings = 15% of 45kW pump = 5,400 kWh/y Nett energy savings = 1,500 kW/y | Assume that a 15% energy efficiency is achieved through the addition of the submersible pump
Reduce irrigation dam evaporation | Irrigation | Water loss from dams due to evaporation is likely to be > 1m per year | Loss reduction | [6 empty] | 0 | N/A | You may expect a 10% reduction in evaporative losses from Duck Weed There are however water quality issues | N/A |  | Controlling evaporative losses from dams NPSI Factsheet April 2005
Reduce dynamic head at the pumps | Irrigation | Rebuild the pump pipe work to be straight flow through with minimum corners and maximum pipe width | Energy efficiency | 2800 |  | 8.6 |  | 0 |  | 597.27 | 4.688 | Doubling the main diameter will result in a 32 fold decrease in the main dynamic head | Total flow through the main is 20 ML/y. Energy saving is 430 kPa x 20,000 kg/y = 8.6 GJ/y Main replacement cost at $28/m | Current duty cycle is full flow 50%, 3/4 flow 25% and 1/2 flow 25% of the time The current flow control system is a throttle valve | Pump World dynamic head calculator http://www.pumpworld.com/total-dynamic-head-calculator.htm
Reduce power demand on irrigation pumps with VSDs | Irrigation | Place VSDs on the major irrigation pumps to reduce power demand and avoid the use of choking valves for variable duty requirements | Energy efficiency | 7700 |  | 42.966 |  |  |  | 2983.9887 | 2.5804 | VSDs can only be added if motors have suitable insulation ratings, or a filter is installed. They will save more energy for variable demand situations | Irrigation pump 37 kW at 80% capacity = 29.6 kW for 28 h/week x 40 w/y gives 33,152 kWh/y Savings with VSD in duty cycle = 36% = 11,935 kWh/y VSD cost at $3,500 + $1,200 pressure meter + $3,000 for installation | $200/kW installation | ETSU Good Practice Guide Vol 2 Energy savings with electric motors and drives
New EC motor for irrigation pump system | Irrigation | Old motors replaced with new efficient EC motors can save up to 5% of the energy consumed | Energy efficiency | 28000 |  | 21.6 |  |  |  | 1500.12 | 18.6652 | EC motor replacing a 75kW old motor may be reduced to 70 kW | 75 kW irrigation pump used 40 h/week 40 weeks per year at 80% capacity uses 96,000 kWh/y. A replacement EC motor rated at 70 kW will use 90,000 kWh/y | 30 kW array to run a 37 kW pump at 80% of capacity Zone 3 STC subsidies apply - total cost per W = $2.50 Utilisation 80% over 300 days = 8h x 25 kW x 300 = 60,000 kWh/y
Solar array to reduce energy consumption and peak demand | Irrigation | Employ solar energy collection with an array on the south bank of the dam | Demand reduction | 75000 |  | 216 |  |  |  | 15001.2 | 4.9996 | Power output is likely to be > 30 kW due to reflection from water surface as well as direct sunlight | Existing 37 kW pumps can be powered through a 30 kW solar system saving the equivalent amount of power from the grid 30 kW array - giving an average 25 kW over 8 hours on 300 days = 60,000 kWh | Assume electricity is available, diesel engine efficiency 35%, electric motor at 90% Diesel coupling by belt drive, electric by direct drive gives another 10% comparative loss. Diesel at $1.40/L and elec at $0.18/kWh
Use electric pumps over diesel where possible | Irrigation | Savings of about 50% of energy and 40% of the cost of pumping are possible in using electric over diesel pumps. | Replace a diesel with an electric pump | 26400 |  | -133.056 | 448 |  | 550 | 7553.7408 | 3.495 | Diesel engines have inherently less than 40% of the efficiency of electric motors The critical factor is availability of electricity supply | 33kW pump motor replaces a 120 HP diesel engine operating 8 hours per day over 25 weeks per year. Diesel engine maintenance is $550/year Cost of elec pump is $400 per kW and installation the same | Cost of PV array with STC subsidy is $2.00 /W including installation and commissioning
Solar system for a pump station | Irrigation | Set up a solar array on the dam wall to gain reflected sunlight from the water as well as direct sunlight. Use this to feed into the pumps used at low pressure for water transfer operations | Renewable energy source | 8000 |  | 8.64 |  |  |  | 600.048 | 13.3323 | Solar arrays are relatively cheap but unreliable as a supply so they can be used for non-critical pumping systems. Utilisation of the energy is critical to cost efficiency | A 4 kW PV array is used to transfer water to an upper dam using a 5 kW low pressure transfer pump. This replaces 50% of the existing mains supply usage of 20 hours per week for 30 weeks per year at 4 kW demand | 200 kPa pump pressure is saved Operation is 1500 hours per yea r 75 kW pump servicing 10 Ha of fixed irrigation Installation cost $75,000.
Use low pressure irrigation systems | Irrigation | Replace highpressure traveller irrigators with hard set or fixed sprinklers systems toreduce pumping pressure | Energy efficiency | 75000 |  | 65 |  |  | 0 | 4514.25 | 16.6141 | Replacement of travellers with fixed irrigation systems will reduce the dynamic head by over 100 kPa | 200 kPa = 200J/L 60 L/s x 200 J/L x 3600 s/h x 1500 h/y = 65 GJ/y at 15c/kWh = $41.7 / GJ | Current main is 75mm and is 100 m long Head at a flow rate of 30 L/sec is 164 m (450 kPa) Main diameter is increased to 150mm head = 1.6 m Total main flow is 20 ML/y | Irrigation Costs and Returns http://www.caswcd.org/Irrigation%20guide/Sec7.pdf
Reduce dynamic head at the pumps | Irrigation | Rebuild the pump pipework to be straight flow through with minimum corners and maximum pipe width | Energy efficiency | 2800 |  | 8.6 | 0 |  | 0 | 597.27 | 4.688 | Doubling the main diameter will result in a 32 fold decrease in the main dynamic head | Total flow through the main is 20 ML/y. Energy saving is 430 kPa x 20,000 kg/y = 8.6 GJ/y Main replacement cost at $28/m. |  | Pump World dynamic head calculator http://www.pumpworld.com/total-dynamic-head-calculator.htm
Clean out main pipe works | Irrigation | Improve flow and reduce frictional losses in main pipe work with maintenance systems (regular disinfection and cleaning) | Energy efficiency | [7 empty] | N/D | The improved performance is dependent on the existing condition of the irrigation works
Diesel pump cooling efficiency | Irrigation | Diesel pump engines can use the irrigation water for engine cooling rather than a radiator and fan |  | 200 |  |  | 2.1616 |  |  | 78.3796 | 2.5517 | Saving quoted at 1%, this comes from removing the need for the motor to drive the fan on the radiator | 5L/hr X 4Hr X 7day X 20 weeks = 2800 L/year @$1.50 / l = $4,200
Rain water collection | Irrigation use | Collection and storage of storm water in a dam reduces the requirement for bore water pumping | Pumping reduction | 5000 | [5 empty] | 0 | N/D | Potential benefit when bore water is a primary source of irrigation water
Movement detector switches in cool stores | Lighting | Replace slow start high bays withrapid start luminaires Link cool store lights to a movement detector | Lighting controls | 2040 |  | 8.46 |  |  |  | 587.547 | 3.4721 | The savings are better if control is added only | Large cool store with 4 high bay lights 4 hours x 4 x 400 W x 250 days/year = 1600 kWh/y savings Lamp savings at 150W replacing 400 W for 12 h/day = 3kwh/d x 250 d/y | Assume 16 hours per day on 6 days per week, 30 weeks per year 4 hours per day saved by switching Cost per luminaire installed = $480 +$120 for switching x 4 luminaires
LED or Inductive high bays linked with sensors | Lighting | Metal halide high bays can be replaced with inductive fluoros to enable fast switch on and sensor controls. The same can be achieved with LED tubes replacing fluoro T8s | Energy efficiency | 600 |  | 8 |  |  |  | 555.6 | 1.0799 | LED lights enable rapid start, longer life and the opportunity to use ambient light level switching | This is the calculation for one lamp. If you have more lamps multiply by the number of lamps. Calculator in work book | Assume 16 hours per day on 6 days per week, 30 weeks per year 4 hours per day saved by switching Cost per luminaire installed = $480 | http://www.ledlightingaustralia.net.au/LED-Tube-Lights-C06/1500-mm-5ftTube25-WATTS-LEDTUBE-1500-25W.html
Replace 400W metal halide high bays with 200W inductively coupled H/Bs | Lighting | Metal halide high bays can be replaced with inductive fluoros and then lux controls can be applied to reduce lighting energy | Energy efficiency + reduction of losses | 360 |  | 2.016 |  |  |  | 140.0112 | 2.5712 | LED lights enable rapid start longer life and the opportunity to use ambient light level switching | 120 W LED can replace a 400 W metal halide high bay with a saving of 280W x 8h/d x 250 d/y = 560 kWh/y per lamp at $360 each | LED high bay at 120W is equivalent to a 400W metal halide high bay Lamps are run 8 hours per day for 250 days per year | http://www.spectrumlighting.com.au/led_hibay_lights.php
Fluoro T8 tube replacement with T5s or LEDs | Lighting | Replace T8s with LED tubes for purpose lighting | Energy efficiency | 1200 |  | 1.3824 |  |  |  | 96.0077 | 12.499 | Lighting design is important and the correct number and location of luminaires is required | A room using 8 x 36W T8 fluoros is replaced with 4 x 24W LED tubes costing $90 each + $210 installation. Used for 40 h per week x 50 weeks per year
Cleaning of electric motors | Maintenance | Clean the air intakes and fins on electric motors | Energy efficiency | [7 empty] | N/D | Motor heating reduces the operating efficiency
Preventative maintenance program | Maintenance | Pump efficiency measurement and target setting for efficiencies | Energy efficiency | 200 |  | 3.1284 |  |  |  | 217.2674 | 0.92052 |  |  | Assume a 2% saving per year
Tractor fuel efficiency monitoring program | Maintenance | Establish efficiency benchmarks for tractor fleet and monitor progress toward efficiency goals | Energy efficiency | 2000 |  |  | 77.2 |  |  | 2799.272 | 0.71447 |  |  | Assume a 2% saving per year
Cold water tank insulation | Processing | Energy savings come from insulation of the tank, the delivery flumes, pipe work and the sides of the elevators | Energy efficiency | 1200 |  | 23.328 |  |  |  | 1620.1296 | 0.74068 | Cold water energy is lost through radiant heating and thermal conduction of steel structures | Conduction Q= k delta T. A/s (where Q is the heat flow, T degrees K, A is the surface area and s is the thickness) = 18x24x0.05/0.02 = 1.1 kW per flanged leg x 4 legs = 4.4 kW Radiation loss at 6C and delta T 24C ~ 150 W/m2 x 12m2 of walls = 1.8 kW for a 10m3 tank Steel pipe work radiative loss = at 150 W/m2 x 0.6 m(200mm pipe) x 10m = 0.9 kW | Assume that insulation application saves 80% of the potential loss through conduction and radiation. Spray on insulation is used with a cost of $30/m2 plus material cost of $30/m2 at a total of 20m2
Equipment switch off at breaks | Processing | One central switch linked to all equipment running on the lines will enable switching off all equipment during breaks | Energy control | 400 |  | 4.5 |  |  |  | 312.525 | 1.2799 | Major savings can be made through switching off motors during breaks. Interconnection of lighting systems may present a problem and two switches may be required | 5kW x 1 h/day x 250 days per year = 1,250 kWh/y is lost 100% saving is achieved by setting up a switch connected to the sub board that is turned off as personnel leave for breaks. Estimated cost is $400 per switch installed | Assume skylights allow 4 hours per day of general lighting switch off. Assume 40 x 150W LED high bays are set up to be switchable by a lux detector
Addition of skylights | Sheds | Improve dark production areas by installing skylights and a linked light switching system to the room lights | Energy efficiency | 11000 |  | 21.6 |  |  |  | 1500.12 | 7.3327 | Skylights can complement high bay lights and allow reduced lighting levels where it is switchable | 40 x 150 W high bays demand 6 kW Switch off of high bays for 4 hours per day saves 6,000 kWh/year Cost of installation of polycarbonate clear roofing over an area of 355m2 =~ $11,000 (incl. Installation) | Assume LED high bays at 150W cost $350 each 4 high bays are replaced with LEDs and skylights are installed at a cost of $4,000 ($40/m2) and lux switches cost $500 installed
Awnings on north facing buildings | Sheds | Install awnings to reduce the heat onto the building and air conditioning loads | Demand reduction | [7 empty] | N/D | Design cost and benefits are dependent on individual circumstances
Solar hot water | Boiler / hot water | Install Solar hot water units on the roof of the factory to supply hot water at 60-90 C to hot water operations. | Alternative energy source | 50000 |  | 281 |  |  |  | 19515.45 | 2.5621 | Requires a use for solar hot water other than domestic service | Thermann 22 solar tube panels at $1,000 each with an area of 3.28 m2 collect 800 W/m2 or 2.6 kW each x 20 panels gives a total output of 52 kW x 6h/d x 250 d/y = 78,000 kWh
|  |  | TOTALS | 1375552 |  | 5185.5161 | 527.3616 | 483.48 | 49302.5 | 413025.7301 | 3.3304
[7 empty] | Total GJ/y | 6196.3577

## Chillers
|  | PLEASE ENTER THE COST TO YOUR BUSINESS (or operational area) OF EACH ENERGY SOURCE |  |  | $/L or kWh | 0.25 | 1.4 | 0.95 |  |  |  | CAPEX / OPEX can be modified as determined in individual cases | Savings are estimated from the actual GJ energy savings + Other savings - OPEX if applicable Payback is calculated from the capital cost / savings per year | Conversion factors: LPG density 0.518 kg/L 0.0257 GJ/L Diesel 0.850 kg/L 0.0386 GJ/L Electricity 0.0036 GJ/kWh
Opportunity Name | Plant Area | Description | Project Type | Project Cost ($) CAPEX | Project cost ($) OPEX | Electricity Savings (GJ/y) | Diesel Savings (GJ/y) | LPG Savings (GJ/y) | Other Savings ($) | Savings ($) | payback years | Comments | Calculation Description | Assumptions | Refs
Chiller fan demand reduction | Chillers | Set up a fan cycling system or VSDs on all fans so that they even out the demand and maintain heat exchange | Cooling efficiency | 526.5 |  | 7.3872 |  | 0 |  | 513.041 | 1.0262 | VSD operating on a bank of 6 x 0.45 kW condenser fans | Evening out of operation save 4% energy VSD saves 15% of energy by fan motors | VSD drives saves 15% energy in the duty cycle Additional savings of 4% are from temperature stabilisation
Chiller VSDs | Chillers | VSDs can be added to the compressors and condenser fans to enable a variable refrigeration supply to the cool rooms | Cooling efficiency | 1940 |  | 13.68 |  | 0 |  | 950.076 | 2.0419 | VSDs can be added to compressor and fan motors as long as they are suitably insulated. If not a filter has to be added | A 10 kW compressor running at 80% of capacity will consume about 20,000 kWh/y at 8kW demand Savings in motor efficiency at a set temperature average 15% with a further 4% savings in on/off losses | All of the waste heat is able to be utilised in the absorption chiller. COP of the conventional compression chillers averages 2.0. | Kirby-Titan information
Investigate possibility of using Absorption Chillers | Chillers | If the site generates waste heat this can be combined with solar heating systems to drive a absorption chiller system | Energy efficiency | 150000 |  | 180 |  | 0 |  | 12501 | 11.999 | Absorption chiller units are all imported and may be considerably cheaper if direct importation is undertaken | The waste heat is estimated at 20% of the heating energy of 2,800 GJ/y. Giving approximately 600 GJ of waste heat in one year. The COP of absorption chillers is about 0.6 and the cost is estimated at $6,000 per kWr. This is assumed to replace 25 kW of conventional chillers
Move from R22 refrigerants | Chillers | Replace R22 with less polluting alternatives | Greenhouse emissions | [6 empty] | 0 | N/A | Phase out of R22 is in progress as it is a strong Greenhouse gas and ozone depleting substance |  | Solar energy collected = 10kW x 2,000 h/year COP of the absorption system is 0.6 Cost of power saved is 25c/kWh
Solar energy absorption chiller system | Chillers | Installation of a solar absorption chiller could be considered to reduce cooling energy use | Energy sources | 60000 | 0 | 43.2 |  | 0 |  | 3000.24 | 19.9984 |  | 10 kW system using evacuated tube panels at $6,000 per kWr | Assume operation of chiller 250 days Chiller cooling at COP = 2.0
Sun shield for chiller units | Chillers | Install a roof over chillers to reduce the heat load on them by reflecting the sun's energy away from the chiller. | Cooling efficiency | 250 |  | 1.0674 |  | 0 |  | 74.1309 | 3.3724 |  | Radiant energy 1120W/m2 at 53% IR Ave 0.593kW/m2 x 2m2 x 6h/d x 250 d/y | Old chiller's COP = 0.7 New scroll compressor COP = 3.0 Actual drive kW at 80%of max.
Chiller unit rationalisation | Chillers | Replace a group of small chillers with one larger unit that is more efficient | Energy efficiency | 21600 |  | 90.7 |  | 0 |  | 6299.115 | 3.4291 | The combination of 3 old 7.5 kWunits into one new 10 kW chiller CAPEX based on Coolpak system 40 plus $4,500 installation | COP for old units at 0.7 and the new unit 3.0 Running both systems at 50% of time over 30 weeks per year | 9 chillers operating at an efficiency COP of 1.5 ave To one chiller with controller at COP of 4.0 | Solar Cooling in Aust. By Kohlenbach and Dennis - Ecolibrium PP32, December 2010
Replacement of old chiller compressors | Chillers | Any chiller system over 15 years old can be economically replaced with a new more efficient unit | Energy efficiency | 4500 |  | 21.6 |  | 0 |  | 1500.12 | 2.9998 | Replacement of a 7 kW compressor at COP of 0.7 with a new 2 kW unit at COP of 3. | A 7 kW compressor at 80% of capacity for 30 h/week x 50 w/y = 8,400 kWh A replacement system at 2 kW for the same operating period = 2,400 kWh Saving = 6,000 kWh =21.6 GJ
Glycol cooling storage | Chillers | Use time of low electrical tariff and periods when solar electricity cannot be used, to store cooling in the form of a glycol or salt block | Energy efficiency and cost efficiency | 9500 |  | 0 |  | 0 |  | 0 | N/D |  |  | Assume: COP of chillers is 1.5 Cost of plumbing and control gear and tank is $800/kW 50 kW of solar power is available for 8 hours per day on weekends
Glycol cool storage 2 | Chillers | Use solar power otherwise wasted to run chillers and generate cool storage in the form of glycol/water ice. Run this back through a heat exchanger to lower the load on chillers | Energy storage | 40000 |  | 145 |  | 0 |  | 10070.25 | 3.9721 | Solar power may be wasted during the weekend or at times of low production. Ice storage in glycol systems may act as energy storage | Chillers run at a total of 50 kW to cool glycol tank over 16 hours during the weekend giving 800 kWh of cooling energy at COP of 1.5 = 1200 kWh or 4.3 GJ of sensible cooling from solar power (min 50 kW PV rating). Savings of 2.9 GJ/week | All compressed air system have leaks, best practices is 3% loses due to leak. The majority of systems have between 20% and 50% loss due to leaks. For the purpose of these calculation we have assumes 30% loss due to leaks.

## Cool stores
|  | PLEASE ENTER THE COST TO YOUR BUSINESS (or operational area) OF EACH ENERGY SOURCE |  |  | $/L or kWh | 0.25 | 1.4 | 0.95 |  |  |  | CAPEX / OPEX can be modified as determined in individual cases | Savings are estimated from the actual GJ energy savings + Other savings - OPEX if applicable Payback is calculated from the capital cost / savings per year | Conversion factors: LPG density 0.518 kg/L 0.0257 GJ/L Diesel 0.850 kg/L 0.0386 GJ/L Electricity 0.0036 GJ/kWh
Opportunity Name | Plant Area | Description | Project Type | Project Cost ($) CAPEX | Project cost ($) OPEX | Electricity Savings (GJ/y) | Diesel Savings (GJ/y) | LPG Savings (GJ/y) | Other Savings ($) | Savings ($) | payback years | Comments | Calculation Description | Assumptions | Refs
Cool room floor insulation | Cool stores | Cooling loss can be reduced with floor insulation using a 10mm rubber roll stuck to the concrete base | Energy efficiency | 3900 | 0 | 280.8 |  | 0 |  | 19501.56 | 0.19998 | Using a cool store with a floor area of 156 m2. | Slab conductance is 230 W/m2 at delta T -= 23 C Addition of 10mm rubber decreases this to 109 W/m2 | COP of refrigeration system is 2.0 COP = 2.0 Chilled water used = 6,000 L/h Filtration and treatment for recycling costs $35,000 + $12,000 per year in chemical and maintenance
Cold water recycling | Cold flumes | Cold water used for hydro coolers and fluming can be filtered and recycled to reduce refrigeration loads | Recycling | 35000 | 12000 | 912 |  | 0 |  | 51338.4 | 0.68175 | This can save significant amounts of refrigeration energy if cold water recycling is not practised | Cooling energy used in cooling unrecycled water is 6,000 L/h x 4.12 kJ/kg.K x T (25-2) = 570 MJ/h. Refrigeration energy is 285 MJ/h. Recycling this water through a filter system saves 80% of this energy = 228 MJ/h = 912 GJ/year | Costs estimated at $15/L and a coverage of 16m2/L with two coats = $188 + painter at $200. | Rotating drum filter systems are available through Wyma
Paint roof white over the cool room and the chillers | Cool stores | White paint will reflect the sun light and lower the temperature gradient between outside and inside | Insulation | 388 |  | 9.6 |  | 0 |  | 666.72 | 0.58195 | Calculation on 100 m2 of roofing | Approximate heat rejection of 178W/m2 for 6h/d x 250 d/y = 267 kWh/y/m2. Over a roof area of 100m2 gives a heat rejection of 26.7 MWh/y . 20% of this removed by cooling system at a COP of 2.0 takes 2,670kWh/y | 2.5 kW fan cost $850 Installation $850 COP of refrigeration chiller = 2.0 | NXTCool Zone from Nutech Paint
Reduce the number of evaporator fans | Cool rooms | Fan heat can be reduced by using less fans with a larger capacity | Energy efficiency | 1700 |  | 2.952 |  | 0 |  | 205.0164 | 8.292 | Calculation for one bank of 6 x 0.45 kW fans at an efficiency of 80% replaced with 1 x 2.5 kW fan at 90% efficiency | Fan energy consumption saving per bank = 10% of 2.7 kW = 0.27 kW Refrigeration load reduction of 0.27 kW of heat per bank /COP of 2.0 = 0.14 kW Cool room operation of 40 hours/week x 50 weeks per year = 820 kWh/y | Chiller operation 50% of the day 7 days x 30 weeks per year at 150 W avoided. Cost of barrel fan and ducting estimated for one room at $1500
Replace room fans with external barrel fans and ducts | Cool stores | Barrel fans external to the cool store reduces heat input to the cool store and enables ducting of air for optimal circulation | Energy efficiency | 1500 |  | 1.3608 |  | 0 |  | 94.5076 | 15.8717 | Cool store evaporative fans produce 15% of energy input into heat in the room | Bank of 4 x 0.25 kW evap. fans add 150W of heat into the room. This requires 214 W of extra cooling energy at a COP of 0.7 costing 5.3c/h. This can be totally avoided by placing the fans outside the cool room | Fans run 70% of 24 h/7d/30 w/y VSD cost = $250/kW + $200/kW installation
Variable speed drive applied to the cool room evaporator fans | Cool stores | The air circulation can be reduced using a VSD on the fans which will reduce cold air loss in the cool room and save energy at the chillers | Energy efficiency | 900 |  | 8.3825 |  | 0 |  | 582.1666 | 1.5459 | Calculation for 2kW of evaporator fans. Power consumption by fans varies as the fan speed cubed | VSD control on evaporator fans saves 4% on stability of temperature control, 25% on fan VSD energy consumption due to VSD control and a further 3.75% due to fan heat reduction. Savings total 33% for a bank of 8 x 0.25 kW fans = 0.66kW |  | http://www.airah.org.au/imis15_prod/Content_Files/EcoLibrium/2013/Apr13/EcoApril13_Forum.pdf
Rapid closing doors on the cool store | Cool stores | Cold air lost when the cool room doors are open during forklift movements in and out can be reduced with rapid closing roller doors | Reduce energy loss | 18000 | 150 | 18.98 |  |  |  | 1168.161 | 15.4088 | Based on a cool room of 700 m3 running continuously at an average ambient temperature of 25 C and a set temperature of 2 C | Savings estimated at 50% of convective losses that total 8% of the total cooling load, calculated at 1.3 GJ/day | Doorway losses are reduced by 30% during opening doorway losses total 8% or 1.3 GJ of cooling load/day
Link evaporator fan operation to door opening | Cool stores | Evaporator fans do not run when the doorway is open as they assist in circulating the air out through the doorway | Reduce energy loss | 400 |  | 7.8 |  | 0 |  | 541.71 | 0.7384 | Reed switch is placed on the door which is connected to the power source for the evaporator fans | Doorway losses of energy are reduced by 30% of 8% of 1.3 GJ/day = 0.0431 GJ/day Cool store operation is during work days (250 per year) Savings = 0.031 x 250 GJ/y = 7.8 GJ/y | Door way energy losses are 1.3 GJ/day
Apply VSD to AHU fans | Cool stores | Use VSDs to reduce AHU fans velocities after cooling and at night | Cooling efficiency | 1177.5 | 0 | 9.5256 |  |  |  | 661.5529 | 1.7799 | Calculation = per AHU fan The need to run AHU fans at peak power diminishes as the produce reaches the desired temperature | VSD installed cost = $195/kW plus temperature control system at $300 which saves an estimated 25% of fan power demand. Assumed fan usage is 50% of time over 35 weeks/y | Heat capacity in total is 150 MJ/K Temperature cycle is 3 K (0.5 over night to 3.5 at end of day) Cost of implementation is PLC on temp control programmable for $5,000
Cycle cool room temperature settings | Cool stores | Increase cooling during the night time and allow cool rooms to rise in temperature during the day to save energy and move consumption to off-peak | Cool room efficiency | 5000 |  | 375 |  |  | 3127.5 | 29171.25 | 0.1714 | Temperature cycling will work when the off-peak tariff operates and there is considerable heat capacity in the cool room contents (ie uninsulated concrete flooring) | Energy savings in cooling = delta T ambient of 15 K x 150 MJ plus Cost savings of extra cooling of 3K x 150 MJ at $27.8/GJ | 70% saving of cold air losses of 35 MJ/day Capital cost $2,500 + $1,500 installation Running cost ( doorway linked) at $200 p.a.
Use of air curtains at cool store openings | Cool stores | Air curtain directed vertically down at entrance to minimise air movement out of the cool store | Cool room efficiency | 4000 | 200 | 6.125 |  | 0 |  | 225.3812 | 17.7477 | Air curtains are more effective in holding cool air than plastic strips and prevent icing up around doorways | 70% of 35 MJ/day x 250 d/.y at $69.44 per GJ | 35 MJ/day losses through the doorway 250 days per year operation 50% savings be using plastic strips
Plastic curtains | Cool stores | Use of plastic strips to prevent air movement when cool room doors are open | Cool room efficiency | 500 | 50 | 4.4 |  | 0 |  | 255.58 | 1.9563 | This calculation is based on 3 air changes per day in the cool room | 3% of energy used to replace losses through the cool room doorways = 35 MJ/day for 250 days per year for a 700 m3 cool room at 2C = 4.4 GJ/y savings | Cost of Peak electricity $0.30 per KW/Hr Off Peak is $0.10 per Kwan hour at present the chiller run use 60% peak and 40% off Peak The new system would run 30% peak and 70% off peak The system use a 10Kw chiller cooling a 15m x 8m @ 1 C Cool room - and use 41, 833 KW/Hr per year | Australian Refrigeration and Air Conditioning Vol 2.
Off-peak and week-end energy storage | Cool stores | An additional thermal store, in the form of frozen glycol or salt, can be established to store solar power when not used by operations. This can be bled back into the cooling system during operations | Energy efficiency and cost efficiency | 9500 |  | 0 |  |  |  | 0 | N/D |  |  | That there is a 0.005% loss of energy when the cool room door is opened when the sensors are tripped by passing traffic. The sensors are tripped 30 times per day over 250 days per year
Set up forklift movement controls | Cool stores | Prevent forklifts inadvertently tripping sensors and opening cool room doors by protecting the sensor area or placing signage on the ground | Loss prevention | 500 |  | 4.7988 |  |  |  | 333.2767 | 1.5003 | Forklift passing traffic can be directed around the door sensors with barriers either side of the door. A less effective alternative is signage painted on the ground where the sensors are | Chillers use 26601KW/hr a year, by stopping unintended door openings a saving of 0.005% can be achieved each time. Cost of electricity is $0.30per kWh | Conduction loss in cool store superstructure 10 kWh/d The cost of construction of internal PU foam walls and ceiling saves 80% of this. Construction cost is $5,000
Old cool store upgrades to improve insulation | Cool stores | Converted cool stores can show high temperature variation on the external cladding. Construction of inner foam walls and ceiling will save energy | Energy efficiency | 5000 |  | 7.2 |  | 0 |  | 500.04 | 9.9992 | Each converted cool store requires individual evaluation of costs and benefits | 10 kWh/day at 250 days operating per year = energy loss 80% of this is saved = 2,000 kWh/y at25c/kWh = $500/y | Losses due to a lack of sealing = 30% of an open doorway = 42 MJ/day 250 operating days per year COP of refrigeration system = 0.7
Truck seal during loading | Dispatch - cool stores | Air leakage during truck loading can be minimised with a flexible sealing system | Energy efficiency | 3500 |  | 4.5 |  | 0 |  | 312.525 | 11.1991 | Sealing losses will be dependent of product movement and the number of trucks loaded as such the cost benefit is uncertain | Sealing saving = Energy losses/day x days /COP of refrigeration system
Demand management system | Electricity supply | Demand management systems are used to shift energy loads from periods of high cost to periods of lower cost. This can be achieved by production planning, peak load shedding and additional sources of energy from solar, wind or batteries | Peak load reduction | [6 empty] | 0 | N/D | This can be a very efficient way of saving energy costs |  | Assume Power factor is corrected from 0.7 to 0.95 on a 100 kVA supply running on average at 50 kVA Peak kVA charge is $10/kW/day Cost of PF correction is $25,000

## Irrigation
|  | PLEASE ENTER THE COST TO YOUR BUSINESS (or operational area) OF EACH ENERGY SOURCE |  |  | $/L or kWh | 0.25 | 1.4 | 0.95 |  |  |  | CAPEX / OPEX can be modified as determined in individual cases | Savings are estimated from the actual GJ energy savings + Other savings - OPEX if applicable Payback is calculated from the capital cost / savings per year | Conversion factors: LPG density 0.518 kg/L 0.0257 GJ/L Diesel 0.850 kg/L 0.0386 GJ/L Electricity 0.0036 GJ/kWh
Opportunity Name | Plant Area | Description | Project Type | Project Cost ($) CAPEX | Project cost ($) OPEX | Electricity Savings (GJ/y) | Diesel Savings (GJ/y) | LPG Savings (GJ/y) | Other Savings ($) | Savings ($) | payback years | Comments | Calculation Description | Assumptions | Refs
Solar bore pumps | Irrigation | Solar bore pumps can be added to the existing dam supply with the saving of bore pump energy and cost | Energy source | 12500 |  | 24.192 |  | 0 |  | 1680.1344 | 7.4399 | Specifically designed solar bore pumps are available and can use direct DC motor to solar panel connections. Operation is only during daylight hours | 5 kW array costs $2.50/W including installation (using STC subsidies) The pump operates 8 hours/day 30 weeks of the year using 6,720 kWh/y at 80% of capacity all of which is saved by the solar system | Conversion to a direct coupling costs $2,000 Power cost at 25c/kWh | NSW Farm Innovation Program 2013 - Solar Pumping Systems
Replace belt drive pump couplings with direct drives | Irrigation | Redesign the pump coupling to direct through a gearbox for belt drives | Energy efficiency | 2000 |  | 16.2 |  |  |  | 1125.09 | 1.7776 | Gear box losses are about 10% of fan belts, so a 10% efficiency loss through a fan belt can be reduced to 1% through a gear box | 55kW pump losses 10% of its efficiency at 55 x 40h x 30weeks/y = 5,000 kWh a gear box direct drive will reduce this to 1% - 500 kWh overall saving is 4,500 kWh/y | Submersible at 5 kW in the river operates 40 h/week and 25 weeks per year at 80% of capacity (dynamic head reduction of 10m = 100 kPa) Pressure pump efficiency raised 15% (45 kW) Submersible pump cost is $2,540 + fitting $1000
Irrigation booster pumps | Irrigation | Install submersible pumps in storages with the pressure pumps on the banks to increase the flow rates | Energy efficiency | 3540 |  | 5.4 |  |  |  | 375.03 | 9.4392 | A low pressure high flow submersible pump can reduce the suction head and improve the main pump performance | Submersible energy consumption = 4,000 kWh/y Pressure pump savings = 15% of 45kW pump = 5,400 kWh/y Nett energy savings = 1,500 kW/y | Assume that a 15% energy efficiency is achieved through the addition of the submersible pump
Reduce irrigation dam evaporation | Irrigation | Water loss from dams due to evaporation is likely to be > 1m per year | Loss reduction | [6 empty] | 0 | N/A | You may expect a 10% reduction in evaporative losses from Duck Weed There are however water quality issues | N/A |  | Controlling evaporative losses from dams NPSI Factsheet April 2005
Reduce dynamic head at the pumps | Irrigation | Rebuild the pump pipe work to be straight flow through with minimum corners and maximum pipe width | Energy efficiency | 2800 |  | 8.6 |  | 0 |  | 597.27 | 4.688 | Doubling the main diameter will result in a 32 fold decrease in the main dynamic head | Total flow through the main is 20 ML/y. Energy saving is 430 kPa x 20,000 kg/y = 8.6 GJ/y Main replacement cost at $28/m | Current duty cycle is full flow 50%, 3/4 flow 25% and 1/2 flow 25% of the time The current flow control system is a throttle valve | Pump World dynamic head calculator http://www.pumpworld.com/total-dynamic-head-calculator.htm
Reduce power demand on irrigation pumps with VSDs | Irrigation | Place VSDs on the major irrigation pumps to reduce power demand and avoid the use of choking valves for variable duty requirements | Energy efficiency | 7700 |  | 42.966 |  |  |  | 2983.9887 | 2.5804 | VSDs can only be added if motors have suitable insulation ratings, or a filter is installed. They will save more energy for variable demand situations | Irrigation pump 37 kW at 80% capacity = 29.6 kW for 28 h/week x 40 w/y gives 33,152 kWh/y Savings with VSD in duty cycle = 36% = 11,935 kWh/y VSD cost at $3,500 + $1,200 pressure meter + $3,000 for installation | $200/kW installation | ETSU Good Practice Guide Vol 2 Energy savings with electric motors and drives
New EC motor for irrigation pump system | Irrigation | Old motors replaced with new efficient EC motors can save up to 5% of the energy consumed | Energy efficiency | 28000 |  | 21.6 |  |  |  | 1500.12 | 18.6652 | EC motor replacing a 75kW old motor may be reduced to 70 kW | 75 kW irrigation pump used 40 h/week 40 weeks per year at 80% capacity uses 96,000 kWh/y. A replacement EC motor rated at 70 kW will use 90,000 kWh/y | 30 kW array to run a 37 kW pump at 80% of capacity Zone 3 STC subsidies apply - total cost per W = $2.50 Utilisation 80% over 300 days = 8h x 25 kW x 300 = 60,000 kWh/y
Solar array to reduce energy consumption and peak demand | Irrigation | Employ solar energy collection with an array on the south bank of the dam | Demand reduction | 75000 |  | 216 |  |  |  | 15001.2 | 4.9996 | Power output is likely to be > 30 kW due to reflection from water surface as well as direct sunlight | Existing 37 kW pumps can be powered through a 30 kW solar system saving the equivalent amount of power from the grid 30 kW array - giving an average 25 kW over 8 hours on 300 days = 60,000 kWh | Assume electricity is available, diesel engine efficiency 35%, electric motor at 90% Diesel coupling by belt drive, electric by direct drive gives another 10% comparative loss. Diesel at $1.40/L and elec at $0.18/kWh
Use electric pumps over diesel where possible | Irrigation | Savings of about 50% of energy and 40% of the cost of pumping are possible in using electric over diesel pumps. | Replace a diesel with an electric pump | 26400 |  | -133.056 | 448 |  | 550 | 7553.7408 | 3.495 | Diesel engines have inherently less than 40% of the efficiency of electric motors The critical factor is availability of electricity supply | 33kW pump motor replaces a 120 HP diesel engine operating 8 hours per day over 25 weeks per year. Diesel engine maintenance is $550/year Cost of elec pump is $400 per kW and installation the same | Cost of PV array with STC subsidy is $2.00 /W including installation and commissioning
Solar system for a pump station | Irrigation | Set up a solar array on the dam wall to gain reflected sunlight from the water as well as direct sunlight. Use this to feed into the pumps used at low pressure for water transfer operations | Renewable energy source | 8000 |  | 8.64 |  |  |  | 600.048 | 13.3323 | Solar arrays are relatively cheap but unreliable as a supply so they can be used for non-critical pumping systems. Utilisation of the energy is critical to cost efficiency | A 4 kW PV array is used to transfer water to an upper dam using a 5 kW low pressure transfer pump. This replaces 50% of the existing mains supply usage of 20 hours per week for 30 weeks per year at 4 kW demand | 200 kPa pump pressure is saved Operation is 1500 hours per yea r 75 kW pump servicing 10 Ha of fixed irrigation Installation cost $75,000.
Use low pressure irrigation systems | Irrigation | Replace highpressure traveller irrigators with hard set or fixed sprinklers systems toreduce pumping pressure | Energy efficiency | 75000 |  | 65 |  |  | 0 | 4514.25 | 16.6141 | Replacement of travellers with fixed irrigation systems will reduce the dynamic head by over 100 kPa | 200 kPa = 200J/L 60 L/s x 200 J/L x 3600 s/h x 1500 h/y = 65 GJ/y at 15c/kWh = $41.7 / GJ | Current main is 75mm and is 100 m long Head at a flow rate of 30 L/sec is 164 m (450 kPa) Main diameter is increased to 150mm head = 1.6 m Total main flow is 20 ML/y | Irrigation Costs and Returns http://www.caswcd.org/Irrigation%20guide/Sec7.pdf
Reduce dynamic head at the pumps | Irrigation | Rebuild the pump pipework to be straight flow through with minimum corners and maximum pipe width | Energy efficiency | 2800 |  | 8.6 | 0 |  | 0 | 597.27 | 4.688 | Doubling the main diameter will result in a 32 fold decrease in the main dynamic head | Total flow through the main is 20 ML/y. Energy saving is 430 kPa x 20,000 kg/y = 8.6 GJ/y Main replacement cost at $28/m. |  | Pump World dynamic head calculator http://www.pumpworld.com/total-dynamic-head-calculator.htm
Clean out main pipe works | Irrigation | Improve flow and reduce frictional losses in main pipe work with maintenance systems (regular disinfection and cleaning) | Energy efficiency | [7 empty] | N/D | The improved performance is dependent on the existing condition of the irrigation works
Diesel pump cooling efficiency | Irrigation | Diesel pump engines can use the irrigation water for engine cooling rather than a radiator and fan |  | 200 |  |  | 2.1616 |  |  | 78.3796 | 2.5517 | Saving quoted at 1%, this comes from removing the need for the motor to drive the fan on the radiator | 5L/hr X 4Hr X 7day X 20 weeks = 2800 L/year @$1.50 / l = $4,200
Rain water collection | Irrigation use | Collection and storage of storm water in a dam reduces the requirement for bore water pumping | Pumping reduction | 5000 | [5 empty] | 0 | N/D | Potential benefit when bore water is a primary source of irrigation water

## Hydro coolers
|  | PLEASE ENTER THE COST TO YOUR BUSINESS (or operational area) OF EACH ENERGY SOURCE |  |  | $/L or kWh | 0.25 | 1.4 | 0.95 |  |  |  | CAPEX / OPEX can be modified as determined in individual cases | Savings are estimated from the actual GJ energy savings + Other savings - OPEX if applicable Payback is calculated from the capital cost / savings per year | Conversion factors: LPG density 0.518 kg/L 0.0257 GJ/L Diesel 0.850 kg/L 0.0386 GJ/L Electricity 0.0036 GJ/kWh
Opportunity Name | Plant Area | Description | Project Type | Project Cost ($) CAPEX | Project cost ($) OPEX | Electricity Savings (GJ/y) | Diesel Savings (GJ/y) | LPG Savings (GJ/y) | Other Savings ($) | Savings ($) | payback years | Comments | Calculation Description | Assumptions | Refs
Hydro cooler plastic blinds | Hydro cooler | Replace plastic strips with pull down plastic blinds to contain the cold water and reduce loss | Energy loss reduction | 500 |  | 40 |  | 0 |  | 2778 | 0.17999 | Losses measured of 10L/min with a temperature of 2C were estimated during hydro cooler operation | Cold water refrigeration losses = 10L/min x 20K x 4.12 kJ/kg.K x 60 min/h = 50 MJ/h Saving 80% of loss = 40 MJ/h / COP of refrigeration of 2.0 = 20 MJ/h = 40 GJ/y of electricity to the chiller | Insulation is 80% efficient at reducing thermal losses. Conductance for SS 18 W/mK Cooling water temp = 2C, steel at 6C and ambient temp = 30C Temperatures maintained for 6,000 h per year. Refrigeration COP = 2.0
Hydro cooler thermal insulation | Hydro cooler | Reduce conductive and radiant losses from steel vessels and pipe work with spray on insulation (PU) and spacer isolation from the floor | Insulation | 12000 |  | 130.464 |  | 0 |  | 9060.7248 | 1.3244 | Various types of insulation can be applied from lagging, to stick-on and spray on insulation. The costs vary and access and cleanliness are key considerations | Conduction Q= k delta T. A/s (where Q is the heat flow, T degrees K, A is the surface area and s is the thickness) = 18x24x0.05/0.02 = 1.1 kW per flanged leg x 8 legs = 8.8 kW Radiation loss at 2C and delta T 24C ~ 150 W/m2 x 30m2 = 4.5 kW for hydro cooler Steel pipe work radiative loss = at 150 W/m2 x 0.6 m(200mm pipe) x 20m = 1.8 kW
Insulation of cooling water pipe work | Hydro cooler | Insulation of exposed cooling water pipes | Insulation | 2400 |  | 30 |  | 0 |  | 2083.5 | 1.1519 |  | The chiller use 41,833 KW/hr a year @ an average cost of $0.25 KW/hr =$10,458.25 | Vessel temperature 6C Vessel surface area = 32 m2 Operation all year = 6,000 h COP of refrigeration system is 2.0 | http://www.engineeringtoolbox.com/thermal-conductivity-d_429.html
Thermal insulation of cold water buffer vessels | Hydro cooler | Insulation of exposed surfaces and stands for cooling vessels | Insulation | 5500 |  | 79.488 |  | 0 |  | 5520.4416 | 0.9963 | Spray insulation should be adequate if access to the steel surfaces is not required | Conduction losses of 1.1kW per stand leg = 4.4 kW Radiant loss from exposed surfaces at 150 W/m2 x 32m2 = 4.8kW 80% saved by insulation of stand and vessel walls | Plastic blind cost = $500 fitted COP refrigeration = 2.0 80% saving of cold water loss through blinds | http://en.wikipedia.org/wiki/List_of_thermal_conductivities
Hydro cooler plastic blinds | Hydro cooler | Replace plastic strips with pull down plastic blinds to contain the cold water and reduce loss | Energy loss reduction | 500 |  | 40 |  | 0 |  | 2778 | 0.17999 | Losses measured of 10L/min with a temperature of 2C were estimated during hydro cooler operation | Cold water refrigeration losses = 10L/min x 20K x 4.12 kJ/kg.K x 60 min/h = 50 MJ/h Saving 80% of loss = 40 MJ/h / COP of refrigeration of 2.0 = 20 MJ/h = 40 GJ/y of electricity to the chiller | Heat capacity 4.12 kJ/kg-K Heat exchanger efficiency 80% Cool water dump weekly Installed cost shell and tube exchanger $10,000
Energy recovery from cold waste | Hydro cooler | Heat exchange waste cold water discharged from the hydro cooler with incoming water into a cold water storage tank | Energy and resource efficiency | 27500 |  | 38 |  | 0 |  | 2639.1 | 10.4202 | The payback will be considerably better if the plumbing and cold water tank are already installed. | 30 m3 of stored water at 2C is dumped per day and exchanged with incoming water at 25C, which is dropped to 15C through a heat exchanger saving 0.96 GJ of energy per dump x 40 dumps per year = 38 GJ/y at a COP of 1.0 for the refrigeration system | Cooling water = 100 kL/day Temperature = 6C outgoing, 20C incoming Exchanger efficiency 46% Cost of exchanger $12,000 + insulated tank = $5,500 + plumbing and controls = $10,000 | Product and Process Design http://www.seas.upenn.edu/~dlewin/FOCAPD_2004/LECTURE_06_Equipment_Sizing_and_Capital_Cost_Estimation.pdf
Cold water heat exchange | Hydro cooler | When chilled water is dumped a heat exchanger can be used to cool feed water into a cold water tank for use across the site | energy recovery | 27500 |  | 334.8 |  | 0 |  | 23251.86 | 1.1827 | This opportunity is applicable if cold water recycling is not practised | Potential energy saved = 100,000 L/d x 4.12 x 14K = 5,880 MJ/day Heat exchanger recovery at 46% = 2,704 MJ/day = 751 kWh/day COP refrigeration system = 2.0 actual refrigeration saving = 372 kWh/day = 93,000 kWh/ 250 day year | Pipe lagging cost $250 and saves 80% of the heat transfer Radiant heat/cool losses 150W/m COP of vac cooler = 1.0 | Product and Process Design http://www.seas.upenn.edu/~dlewin/FOCAPD_2004/LECTURE_06_Equipment_Sizing_and_Capital_Cost_Estimation.pdf
Insulation of cooling water pipe work | Hydro vac cooler | Insulation of exposed cooling water pipes | Insulation | 250 |  | 0.648 |  | 0 |  | 45.0036 | 5.5551 |  | 150 W x 5 m x 2h/day x 150 days/y = 225 kWh/y saving 80% = 180 kWh/y | 5 kW bore pump utilising a 5 kW array Providing useful water to a dam 80% of the year Replacement of the same pump using electrical supply | http://www.engineeringtoolbox.com/thermal-conductivity-d_429.html

## Other operations
|  | PLEASE ENTER THE COST TO YOUR BUSINESS (or operational area) OF EACH ENERGY SOURCE |  |  | $/L or kWh | 0.25 | 1.4 | 0.95 |  |  |  | CAPEX / OPEX can be modified as determined in individual cases | Savings are estimated from the actual GJ energy savings + Other savings - OPEX if applicable Payback is calculated from the capital cost / savings per year | Conversion factors: LPG density 0.518 kg/L 0.0257 GJ/L Diesel 0.850 kg/L 0.0386 GJ/L Electricity 0.0036 GJ/kWh
Opportunity Name | Plant Area | Description | Project Type | Project Cost ($) CAPEX | Project cost ($) OPEX | Electricity Savings (GJ/y) | Diesel Savings (GJ/y) | LPG Savings (GJ/y) | Other Savings ($) | Savings ($) | payback years | Comments | Calculation Description | Assumptions | Refs
Electric forklifts | Alternative energy sources | Electric forklifts can be charged on weekends and evenings for day operations with the aid of battery system and PV back-up | Energy storage | 20000 | 250 | -36.9 |  | 109.225 | 1500 | 2723.7049 | 7.3429 | Costs and savings are per electric forklift operating 250 x8 hour shifts per year | 41 kWh/shift (service $250/y) LPG 17 L/shift (service $1500/y) | 25c/kWh = $69.44/GJ and LPG $1/L = $38.9/GJ | Yale Materials Handling Corp.
Solar panels on roof | Alternative energy sources | Reduce peak electricity demand with solar generation | Demand reduction | 40000 | 0 | 129.6 |  |  |  | 9000.72 | 4.4441 | 20 kW system installed | $2/W installed, 6h/day over 300 d/y x 20 y | 25c/kWh = $69.44/GJ all solar energy replaces that bought from the grid
Wind power source | Alternative energy sources | Reduce peak electricity demand with wind generation | Demand reduction | 390000 | 20000 | 1420 |  |  |  | 78619 | 4.9606 | Wind requirements are critical to economics of wind generation - need 20% of capacity at 4.5 to 5 m/s | Capital cost of a 225 kW system = $390,000 Subsidies LGCs continue at 2014 rate | Assume 20% of capacity achieved Cost per kW for a second hand system of $1,750/kW OPEX at 5% p.a.
Batteries for energy storage | Alternative energy sources | Spread the electricity demand using Lithium Ion batteries 100 kWh system installed | Demand reduction | 100000 | 1000 | 108 |  |  |  | 6500.6 | 15.3832 | Additional savings may be made by reducing peak demand charges. CAPEX reduction is likely as battery production increases | Total energy saved and reused = 100*0.9*5000 = 450,000 kWh = 30,000 kWh/y = 108 GJ/y Cost = $10 x 100 kWh = $1000/y | 1 cycle per day to 90% of capacity over 5,000 cycles Battery efficiency 90% O&M cost of $10/kWh/y Cost of LIB at $1000/kWh and cost of power dsicounted from a solar or wind system. | http://theenergycollective.com/schalk-cloete/421716/seeking-consensus-internalized-costs-energy-storage-batteries
Blowdown heat recovery | Boiler | Install a flash vessel to recover waste heat from boiler blow down | Energy Efficiency | 8500 |  |  |  | 85.32 |  | 3153.0006 | 2.6958 | Energy savings and paybacks are dependent on the size of the boiler system employed |  | LPG usage on site is assumed 80% of this is use by a boiler and the rest been used by forklifts. The saving are estimated at 3% for the installation of a Flash vessel, this is the industry norm | saving based on Best Practice Guide Steam, Hot Water & Process Heating -- Sustainability Vic
Boiler Management system | Boiler | Install a Boiler Management system that controls the air to fuel mixture to ensure complete consumption of fuel | Energy Efficiency | 10500 |  |  |  | 142.2 |  | 5255.001 | 1.9981 | Energy savings and paybacks are dependent on the size of the boiler system employed |  | The saving are estimated at 5% for the installation of a boiler management system | saving based on Best Practice Guide Steam, Hot Water & Process Heating -- Sustainability Vic
Economisers | Boiler | Install an Economiser is to the boiler flue, to recover waste heat. The waste heat could be used to pre heat boiler make up water | Energy efficiency | 12200 |  |  |  | 142.2 |  | 5255.001 | 2.3216 | Energy savings and paybacks are dependent on the size of the boiler system employed |  | The savings are estimated at 5% for the installation of an economiser, this is an industry norm | saving based on Best Practice Guide Steam, Hot Water & Process Heating -- Sustainability Vic
Pre heat combustion air | Boiler | Use waste heat to pre heat combustion air before feeding in to the boiler | Energy efficiency | 4500 |  |  |  | 56.88 |  | 2102.0004 | 2.1408 | Energy savings and paybacks are dependent on the size of the boiler system employed |  | The saving are estimated at 2% for installation of combustion air pre heating
Total dissolved solids (TDS) control, and boiler blowdown | Boiler | Install automated TDS control system, to reduce the amout of blow down required. Saving both energy, and boiler treatment chemicals | Energy and water efficiency | 3560 |  |  |  | 56.88 |  | 2102.0004 | 1.6936 | Energy savings and paybacks are dependent on the size of the boiler system employed |  | VSD drive $525 / 5.5 kW = $95/kW Installation and control = $100/kW The saving are estimated at 2% from the installation of a TDS control system. This doesn't take into account the saving in boiler chemicals
Demand management system | Electricity supply | Demand management systems are used to shift energy loads from periods of high cost to periods of lower cost. This can be achieved by production planning, peak load shedding and additional sources of energy from solar, wind or batteries | Peak load reduction | [6 empty] | 0 | N/D | This can be a very efficient way of saving energy costs |  | Assume Power factor is corrected from 0.7 to 0.95 on a 100 kVA supply running on average at 50 kVA Peak kVA charge is $10/kW/day Cost of PF correction is $25,000
Power Factor correction | Electricity supply | Peak demand can be reduced by applying capacitors to compensate for reactive load | Peak load reduction | 25000 |  | 0 |  | 0 | 45625 | 45625 | 0.54795 | Power factor correction economics depend on demand costs and the state of the power factor before correction | Cost savings = 100*0.25*10*365/2
Heat exchange cold water with incoming fresh water | Flumes | Use chilled water wastes to cool incoming town water and reduce the load on chillers cooling incoming water | Energy usage efficiency | 7500 |  | 25.6 |  | 0 |  | 1777.92 | 4.2184 |  |  | Plastic blind cost = $500 fitted COP refrigeration = 2.0 80% saving of cold water loss through blinds
Movement detector switches in cool stores | Lighting | Replace slow start high bays withrapid start luminaires Link cool store lights to a movement detector | Lighting controls | 2040 |  | 8.46 |  |  |  | 587.547 | 3.4721 | The savings are better if control is added only | Large cool store with 4 high bay lights 4 hours x 4 x 400 W x 250 days/year = 1600 kWh/y savings Lamp savings at 150W replacing 400 W for 12 h/day = 3kwh/d x 250 d/y | Assume 16 hours per day on 6 days per week, 30 weeks per year 4 hours per day saved by switching Cost per luminaire installed = $480 +$120 for switching x 4 luminaires
LED or Inductive high bays linked with sensors | Lighting | Metal halide high bays can be replaced with inductive fluoros to enable fast switch on and sensor controls. The same can be achieved with LED tubes replacing fluoro T8s | Energy efficiency | 600 |  | 8 |  |  |  | 555.6 | 1.0799 | LED lights enable rapid start, longer life and the opportunity to use ambient light level switching | This is the calculation for one lamp. If you have more lamps multiply by the number of lamps. Calculator in work book | Assume 16 hours per day on 6 days per week, 30 weeks per year 4 hours per day saved by switching Cost per luminaire installed = $480 | http://www.ledlightingaustralia.net.au/LED-Tube-Lights-C06/1500-mm-5ftTube25-WATTS-LEDTUBE-1500-25W.html
Replace 400W metal halide high bays with 200W inductively coupled H/Bs | Lighting | Metal halide high bays can be replaced with inductive fluoros and then lux controls can be applied to reduce lighting energy | Energy efficiency + reduction of losses | 360 |  | 2.016 |  |  |  | 140.0112 | 2.5712 | LED lights enable rapid start longer life and the opportunity to use ambient light level switching | 120 W LED can replace a 400 W metal halide high bay with a saving of 280W x 8h/d x 250 d/y = 560 kWh/y per lamp at $360 each | LED high bay at 120W is equivalent to a 400W metal halide high bay Lamps are run 8 hours per day for 250 days per year | http://www.spectrumlighting.com.au/led_hibay_lights.php
Fluoro T8 tube replacement with T5s or LEDs | Lighting | Replace T8s with LED tubes for purpose lighting | Energy efficiency | 1200 |  | 1.3824 |  |  |  | 96.0077 | 12.499 | Lighting design is important and the correct number and location of luminaires is required | A room using 8 x 36W T8 fluoros is replaced with 4 x 24W LED tubes costing $90 each + $210 installation. Used for 40 h per week x 50 weeks per year
Cleaning of electric motors | Maintenance | Clean the air intakes and fins on electric motors | Energy efficiency | [7 empty] | N/D | Motor heating reduces the operating efficiency
Preventative maintenance program | Maintenance | Pump efficiency measurement and target setting for efficiencies | Energy efficiency | 200 |  | 3.1284 |  |  |  | 217.2674 | 0.92052 |  |  | Assume a 2% saving per year
Tractor fuel efficiency monitoring program | Maintenance | Establish efficiency benchmarks for tractor fleet and monitor progress toward efficiency goals | Energy efficiency | 2000 |  |  | 77.2 |  |  | 2799.272 | 0.71447 |  |  | Assume a 2% saving per year
Cold water tank insulation | Processing | Energy savings come from insulation of the tank, the delivery flumes, pipe work and the sides of the elevators | Energy efficiency | 1200 |  | 23.328 |  |  |  | 1620.1296 | 0.74068 | Cold water energy is lost through radiant heating and thermal conduction of steel structures | Conduction Q= k delta T. A/s (where Q is the heat flow, T degrees K, A is the surface area and s is the thickness) = 18x24x0.05/0.02 = 1.1 kW per flanged leg x 4 legs = 4.4 kW Radiation loss at 6C and delta T 24C ~ 150 W/m2 x 12m2 of walls = 1.8 kW for a 10m3 tank Steel pipe work radiative loss = at 150 W/m2 x 0.6 m(200mm pipe) x 10m = 0.9 kW | Assume that insulation application saves 80% of the potential loss through conduction and radiation. Spray on insulation is used with a cost of $30/m2 plus material cost of $30/m2 at a total of 20m2
Equipment switch off at breaks | Processing | One central switch linked to all equipment running on the lines will enable switching off all equipment during breaks | Energy control | 400 |  | 4.5 |  |  |  | 312.525 | 1.2799 | Major savings can be made through switching off motors during breaks. Interconnection of lighting systems may present a problem and two switches may be required | 5kW x 1 h/day x 250 days per year = 1,250 kWh/y is lost 100% saving is achieved by setting up a switch connected to the sub board that is turned off as personnel leave for breaks. Estimated cost is $400 per switch installed | Assume skylights allow 4 hours per day of general lighting switch off. Assume 40 x 150W LED high bays are set up to be switchable by a lux detector
Addition of skylights | Sheds | Improve dark production areas by installing skylights and a linked light switching system to the room lights | Energy efficiency | 11000 |  | 21.6 |  |  |  | 1500.12 | 7.3327 | Skylights can complement high bay lights and allow reduced lighting levels where it is switchable | 40 x 150 W high bays demand 6 kW Switch off of high bays for 4 hours per day saves 6,000 kWh/year Cost of installation of polycarbonate clear roofing over an area of 355m2 =~ $11,000 (incl. Installation) | Assume LED high bays at 150W cost $350 each 4 high bays are replaced with LEDs and skylights are installed at a cost of $4,000 ($40/m2) and lux switches cost $500 installed
Awnings on north facing buildings | Sheds | Install awnings to reduce the heat onto the building and air conditioning loads | Demand reduction | [7 empty] | N/D | Design cost and benefits are dependent on individual circumstances
Solar hot water | Boiler / hot water | Install Solar hot water units on the roof of the factory to supply hot water at 60-90 C to hot water operations. | Alternative energy source | 50000 |  | 281 |  |  |  | 19515.45 | 2.5621 | Requires a use for solar hot water other than domestic service | Thermann 22 solar tube panels at $1,000 each with an area of 3.28 m2 collect 800 W/m2 or 2.6 kW each x 20 panels gives a total output of 52 kW x 6h/d x 250 d/y = 78,000 kWh

## Top Ten
Top Ten Quick energy saving opportunities
Opportunity Name | Plant Area | Description | Project Type | Project Cost ($) CAPEX | Project cost ($) OPEX | Electricity Savings (GJ/y) | Other Savings ($) | Savings ($) | payback years | Comments | Calculation Description | Assumptions | Refs
Cool room floor insulation | Cool stores | Insulation and cooling loss can be reduced with floor insulation using a 10mm rubber roll stuck to the concrete base | Energy efficiency | 3900 |  | 280.8 | 0 | 19487.52 | 0.20013 | Using a cool store with a floor area of 156 m2. | Slab conductance is 230 W/m2 at delta T -= 23 C Addition of 10mm rubber decreases this to 109 W/m2 | COP of refrigeration system is 2.0 COP = 2.0 Chilled water used = 6,000 L/h Filtration and treatment for recycling costs $35,000 + $12,000 per year in chemical and maintenance
Paint roof white over the cool room and the chillers | Cool stores | White paint will reflect the sun light and lower the temperature gradient between outside and inside | Insulation | 388 |  | 9.6 | 0 | 666.24 | 0.58237 | Calculation on 100 m2 of roofing. | Approximate heat rejection of 178W/m2 for 6h/d x 250 d/y = 267 kWh/y/m2. Over a roof area of 100m2 gives a heat rejection of 26.7 MWh/y . 20% of this removed by cooling system at a COP of 2.0 takes 2,670kWh/y | 2.5 kW fan cost $850 Installation $850 COP of refrigeration chiller = 2.0 | NXTCool Zone from Nutech Paint
Link evaporator fan operation to door opening | Cool stores | Evaporator fans are stopped when the doorway is open to reduce cold air losses | Reduce energy loss | 400 |  | 7.8 | 0 | 541.32 | 0.73893 | Reed switch is placed on the door which is connected to the power source for the evaporator fans. | Doorway losses of energy are reduced by 30% of 8% of 1.3 GJ/day = 0.0431 GJ/day Cool store operation is during work days (250 per year) Savings = 0.031 x 250 GJ/y = 7.8 GJ/y | 25c/kWh = cost of power
Cycle cool room temperature settings | Cool stores | Increase cooling during the night time and allow cool rooms to rise in temperature during the day to save energy and move consumption to off-peak. | Cool room efficiency | 5000 |  | 375 | 3127.5 | 26025 | 0.19212 | Temperature cycling will work when the off-peak tariff operates and there is considerable heat capacity in the cool room contents (ie uninsulated concrete flooring). | Energy savings in cooling = delta T ambient of 15 K x 150 MJ plus Cost savings of extra cooling of 3K x 150 MJ at $27.8/GJ | 70% saving of cold air losses of 35 MJ/day Capital cost $2,500 + $1,500 installation Running cost ( doorway linked) at $200 p.a.
Thermal insulation of cold water buffer vessels | Hydro cooler | Insulation of exposed surfaces and stands for cooling vessels | Insulation | 5500 |  | 79.488 | 0 | 5516.4672 | 0.99701 | Spray insulation should be adequate if access to the steel surfaces is not required. | Conduction losses of 1.1kW per stand leg =4.4 kW Radiant loss from exposed surfaces at 150 W/m2 x 32m2 = 4.8kW80% saved by insulation of stand and vessel walls | Plastic blind cost = $500 fitted COP refrigeration = 2.0 80% saving of cold water loss through blinds | http://en.wikipedia.org/wiki/List_of_thermal_conductivities
Improve pump couplings | Irrigation | Efficiency improvement by redesigning the pump coupling to direct through a gearbox | Energy efficiency | 2000 |  | 16.2 |  | 1124.28 | 1.7789 | Gear box losses are about 10% of fan belts, so a 10% efficiency loss through a fan belt can be reduced to 1% through a gear box | 55kW pump losses 10% of its efficiency at 55 x 40h x 30weeks/y = 5,000 kWh a gear box direct drive will reduce this to 1% - 500 kWh overall saving is 4,500 kWh/y | Submersible at 5 kW in the river operates 40 h/week and 25 weeks per year at 80% of capacity (dynamic head reduction of 10m = 100 kPa) Pressure pump efficiency raised 15% (45 kW) Submersible pump cost is $2,540 + fitting $1000
Reduce power demand on irrigation pumps with VSDs | Irrigation | Place VSDs on the major irrigation pumps to reduce power demand and avoid the use of choking valves | Energy Efficiency | 7700 |  | 42.966 | 0 | 2981.8404 | 2.5823 | VSDs can only be added if motors have suitable insulation ratings, or a filter is installed. They will save more energy for variable demand situations. | Irrigation pump 37 kW at 80% capacity = 29.6 kW for 28 h/week x 40 w/y gives 33,152 kWh/y Savings with VSD in duty cycle = 36% = 11,935 kWh/y VSD cost at $3,500 + $1,200 pressure meter + $3,000 for installation | $200/kW installation | ETSU Good Practice Guide Vol 2 Energy savings with electric motors and drives
Movement detector switches in cool stores | Lighting | Establish a movement detector switch and lamp replacement to instantaneous ON type. | Lighting controls | 2040 |  | 8.46 |  | 587.124 | 3.4746 | Large cool store with 4 high bay lights The savings are better if control is added only | 4 hours x 4 x 400 W x 250 days/year = 1600 kWh/y savings Lamp savings at 150W replacing 400 W for 12 h/day = 3kwh/d x 250 d/y | Assume 16 hours per day on 6 days per week, 30 weeks per year 4 hours per day saved by switching Cost per luminaire installed = $480 +$120 for switching x 4 luminaires
LED or Inductive high bays linked with sensors | Lighting | Metal halide high bays can be replaced with inductive fluoros to enable fast switch on and sensor controls. The same can be achieved with LED tubes replacing fluoro T8s. | Energy efficiency | 360 |  | 1.8 |  | 124.92 | 2.8818 | LED lights enable rapid start longer life and the opportunity to use ambient light level switching. | 150 W LED can replace a 400 W metal halide high bay with a saving of 250W x 8h/d x 250 d/y = 500 kWh/y
Equipment switch off at breaks | Processing | A central switch to all equipment running on the lines will enable savings of equipment running during breaks | Energy control | 400 |  | 4.5 | 0 | 312.3 | 1.2808 | Major savings are through motors switched off during breaks. Interconnection of lighting systems may present a problem and two switches may be required. | 5kW x 1 h/day x 250 days per year = 1,250 kWh/y is lost 100% saving is achieved by setting up a switch connected to the sub board that is turned off as personnel leave for breaks. Estimated cost is $400 per switch installed. | Assume skylights allow 4 hours per day of general lighting switch off. Assume 40 x 150W LED high bays are set up to be switchable by a lux detector